Electrical Load Worksheet

The following worksheet may be used to calculate electrical loads for EVCS installed at existing Single-Family Dwellings only.  For other occupancies or projects with different scopes of work, load calculations are required to be prepared by a licensed electrical engineer or electrical contractor displaying conformance with the applicable code requirements and load calculation methodology.

INSTRUCTIONS: Review the list of electrical loads in the table below and check () all that exist in the home.  For each item checked, fill in the corresponding “Watts Used” (refer to the “Typical Usage” column.)  If multiple instances of the load exist be sure to multiply the load by the number of instances.  Add up all of the numbers in the “Watts Used” column and write that number in the “TOTAL WATTS” space at the bottom of the table.

Loads shown are estimates; actual loads may vary.  For a more accurate analysis, use the nameplate ratings of appliances and other loads.  This is a voluntary compliance alternative and the applicant may wish to consult with a licensed electrical professional.  Use of this electrical load calculation worksheet is at the user’s risk and carries no implied warranty or guarantee of accuracy. This worksheet assumes that the existing electrical system at the premises is code-compliant, sized properly, and in good functioning order with no signs of damage or disrepair.

| Check All Applicable Loads | Description of Load | Typical Usage | Watts Used |
| --- | --- | --- | --- |
| GENERAL LIGHTING AND RECEPTACLE OUTLET CIRCUITS |  |  |  |
|  | Multiply the dwelling square footage by 3 | 3 watts/sq. ft. |  |
| KITCHEN CIRCUITS |  |  |  |
|  | Kitchen circuits | 3,000 watts | 3,000 (minimum) |
|  | Electric oven | 2,000 watts |  |
|  | Electric stove top | 5,000 watts |  |
|  | Microwave | 1,500 watts |  |
|  | Garbage disposal under kitchen sink | 1,000 watts |  |
|  | Automatic dishwasher | 3,500 watts |  |
|  | Garbage compactor | 1,000 watts |  |
|  | Instantaneous hot water at sink | 1,500 watts |  |
| LAUNDRY CIRCUIT |  |  |  |
|  | Laundry circuit | 1,500 watts | 1,500 (minimum) |
|  | Electric clothes dryer | 5,000 watts |  |
| HEATING AND AIR CONDITIONING CIRCUITS |  |  |  |
|  | Central heating (gas) and air conditioning | 6,000 watts |  |
|  | Window mounted A/C | 1,000 watts |  |
|  | Whole-house or attic fan | 500 watts |  |
|  | Evaporative cooler | 500 watts |  |
| OTHER ELECTRICAL LOADS |  |  |  |
|  | Electric water heater (storage type) | 4,000 watts |  |
|  | Electric tankless water heater | 15,000 watts |  |
|  | Swimming pool or spa | 3,500 watts |  |
|  | Other (describe): |  |  |
|  | Other: |  |  |
|  | Other: |  |  |
| ELECTRIC VEHICLE CHARGER CIRCUIT |  |  |  |
|  | EVCS rating in Amps X 125% X Volts |  |  |

TOTAL WATTS = _________________

To determine the minimum size service panel and main service breaker needed (measured in amps), take Total Watts from above and divide by 240.  Example: 30,000 watts / 240 volts equals 125 amp main service needed.

Size of existing Main Service Breaker = ________ Size needed from calculation above = _________